## Slide 1
Ring magnet system —Power supplies—
T. Oki
T. Adachi
T. Kawamoto
S. Nakamura
21th KEKB Accelerator Review Committee

## Slide 2
Newly fabricated or old power supplies for Main Ring
Output power | Newly fabricated PS | Reused PS (#overhauled) | 
0.95 MW | 2 | 0 | Main dipoles
0.4-1 MW | 9 | 0 | Wigglers
0.1-0.5 MW | 0 | 18# | Main quadrupoles
2-105 kW | 92 | 335# | Bend./Quad./Sext.
0.3-2.4 kW | 138 | 1681 | Steering magnets/ corrector coils
Total | 359 | 2034 | 
List of Magnet power supplies
2kA, 15V | 2+6* | 0 | QCS Main quads.
<500 A, 20 V | 3* | 0 | QCS Solenoids
±70A, ±10V | 45 | 0 | QCS correction coils
・ Newly fabricated or to be fabricated (*) QCS power supplies

## Slide 3
Start up: system check and full power load test
Full-scale start-up tasks such as network test, interlock system test, full power load test, cable connection check to avoid abnormal heating, polarity check, magnet standardization test and so on were completed before Feb.8 beam injection to the MR.

## Slide 4
Old medium-class power supplies were overhauled. Replacement of chemical capacitors, AC-DC converters, circuit breakers and IGBTs was performed.
In order to reduce switching noise, ceramic capacitors are added at the output terminal. Switching noise is reduced to 1/20.
Test example 1/2 —switching noise
0.1 V/div
10 μs/div
VP
VN
W/ 1 μF capacitor
VP
VN
5 V/div
10 μs/div
W/O capacitor
Ceramic capacitors

## Slide 5
Newly fabricated medium class power supplies were designed to be lower current ripples. Histograms of current ripples are compared with the results of old (overhauled) power supply.
Test example 2/2 —ripples
50 Hz
Overhauled 335 of old PS
Newly fabricated 92 of PS
1 ppm
0.6 ppm
5 ppm
0.2 ppm
#of PS’s
#of PS’s

## Slide 6
Magnet power supply system works well except for following failures occurred up to now.
First Commissioning in Phase 1
Failures in Large class PS | # of event | comment
AC input over current | 3 | AC distortion (RF system crowbar work)
AC input over current | 6 | AC distortion (VAR system# work in line facility)
AC input Stop, CB Fault | 2 | Earthquake
Failures in Medium class PS | # of event | comment
Thermostat | 4 | Thermal control equipment was repaired.
Over current (IGBT modules) | 2 | Modules were replaced. Repaired.
Cable GND fault | 1 | The fault cable was disconnected.
Tracking error | 1 | Fault in the polarity inversion circuit. Repaired.
Failures in small class PS | # of event | comment
DC-DC board failure Output over voltage etc. | 17 | Power supplies themselves were replaced.
#) Compensation system for a reactive power in the AC power distribution facility. AC line phase-advancing capacitor equipment was automatically controlled. However, unexpected operation occurred in early stage of Phase 1. Since capacitors has been manually operated, failures doesn't occur.

## Slide 7
How the system works well? Current stability of Main dipole magnet power supply is compared with one of KEKB.
First Commissioning in Phase 1-cont.
0.5 mA
1.3 ppm(p-p)/week
5 mA
~20 ppm(p-p)/week
KEKB (1250 A, 770 V)
standardization
1 week
1 week
standardization
SuperKEKB (860 A, 1100 V)

## Slide 8
As Funakoshi-san and Sugimoto-san reported: in order to compensate a leak field of a lambertson magnet, additional coils of SX and skew Q magnet were wound/ applied for this purpose.
As Funakoshi-san and Suetsugu-san reported: Solenoid coils were tentatively wound over LER vacuum chamber by vac. group, and small class power supplies also support to drive it.
Two prompt contributions to Phase 1 commissioning
Y. Suetsugu (IPAC16)
Shift report (April. 8)

## Slide 9
SLAC Dithering coils for IP horizontal collision feedback system were installed.
Power supplies were also installed, and cabling for the coils were completed. Magnetic polarity check was done.
Preparations for Phase 2: IP collision feedback system
Coil installation was performed with U. Wienands, SLAC.

## Slide 10
Many works are in progress to be ready for the QCS operation, which starts in Nov. 2016 for L-side or Feb. 2017 for R-side.
  Power supplies
    Prototype power supply for both of main and corrector coils was developed. Mass production and fabrication of anti-solenoid PS’s has been carried out.
Cabling
    Cable laying work from PS building to IR was completed. Work for the connection of the cables to PS’s or QCS is planed in this summer.
Facility for power supply
    AC power distribution board and water cooling system has been designed. These will be ready by the end of this Oct.
Interlock/monitor system
    PLC system has been fabricated, and will be derived by the end of this July.
Preparations for Phase 2: QCS power supply system

## Slide 11
QCS cable laying work
Cables were laid from PS building…
through vertical shafts…
and cable rack to the interaction region…
Cables to be connected with QCS magnets

## Slide 12
Aiming spec.
Rated output | DC 2 kA, 10 V
Current setting resolution | < 0.1 ppm
Current stability | < 2 ppm/8 hrs.
Current ripple (< 10kHz) | < 1 ppm (rms)
Current noise (> 10kHz) | < 1 ppm (0-peak)
(1) For low ripple and noise: Symmetric structure
A full-scale prototype of QCS power supply
DCCTs on both output terminals.
Symmetric circuit structure with respect to ground.
Shielded high-frequency transformer

## Slide 13
Digital feedback control for QCS power supply
(2) For high stability: Digital feedback with 24-bit control board
+
N
P
DCCT(N)
8.5-digit DMM
Major setting value (20 bits)
DAC
Error
Minor setting value (4 bits)
DAC
1/24
+
+
+
-
Analog current control loop
-
-
+
1/2
1/2
Output terminal
Digital feedback loop
24-bit control board
DCCT(P)
Two 20bit DACs
(AD5791)

## Slide 14
Temp. coefficients of the system
0.125 ppm/K (AD5791 DAC with Buffer amps.)
0.3 ppm/K (Keithley 2002)
1.5 ppm/K (TOPACC) (or 0.5 ppm/K (TOPACC optional))
---------
Total: 1.925 ppm/K
Constant climate chamber keeps temp. within 0.2 deg.
→ 0.385 ppm for 0.2 deg

## Slide 15
Test result of the digital feedback system
Performed by using a medium-class power supply (15 V, 500 A).
Test result of QCS prototype: 1.9 ppm (p-p)/8 hrs.
Ripple, noise, quench protection test, etc :OK.
→Mass production has been carried out.
1 hour
Output current measured by DCCT (0.25 mA/div)
Digital feedback loop well corrects DAC input by 24bit resolution
8 hrs.
1.9 ppm

## Slide 16
45 of QCS corrector power supplies was fabricated.
Rated output | DC ± 70 A, 10 V
Current setting resolution | < 1 ppm
Current stability | < 5 ppm/8 hrs.
Current ripple (< 10kHz) | < 5 ppm (rms)
Current noise (> 10kHz) | < 5 ppm (0-peak)
QCS corrector power supply
Test results: Stability 2.1 ppm/24 hrs. with temp. coeff. of 0.6 ppm/℃
12.34 ppm
20.5 ℃
24 hrs.
Ripple, noise, quench protection test and so on: also OK.

## Slide 17
Summary
Magnet power supply system was integrated and finished before Phase 1. Where the full-scale start-up tasks were completed.
In the full-scale load test, both the old and newly fabricated medium-class power supplies showed low ripple and low noise characteristic, successfully.
Magnet power supply system has been worked well during Phase 1 commissioning except for several minor failures. The current stability of main dipole power supply should be remarkably mentioned.
Preparations for Phase 2 have been in progress. Dithering coils for the IP collision feedback system and power supplies have been already installed.
For the QCS system, many works are in progress to be ready for the QCS operation, which starts in Nov. 2016 for L-side or Feb. 2017 for R-side.